## Index
INDEX | Technology Data for Indian Power Plants - first edition
01a Coal fired, subcritical power plant | All cost data is in 2020₹ (INR) | Exchange rate EUR to INR (1 to 86.6)
01b Coal fired, supercritical power plant |  | Exchange rate USD to INR (1 to 72.4)
01c Coal fired, ultra-supercritical power plant
02a Gas turb. open cycle
02b Gas turb. combined cycle
02c Gas engines
03 Biomass plant
04 Onshore turbines
05 Offshore turbines
06a Large scale utility scale Photovoltaics
06b Rooftop Photovoltaics
07a Run-of-river w/o storage
07b Run-of-river w/storage
07c Small Reservoir Hydro Power (<25 MW)
07d Large Reservoir Hydro Power (>25 MW)
07e Pumped storage (on-river)
07f Pumped storage (closed loop)
8a Nuclear, Pressurized heavy-water reactor
8b Nuclear, Light-water reactor
09 Battery storage
This file contains the technology data sheets related to the first technology catalogue for India. As this is the first technology catalogue, it will focus on key power generation technologies, while further technology catalogues could include power transmissions or additional storage technologies.
This technology catalogue is therefore designed to describe some key technologies for the current and the future power system in India, but not to go into details with certain subtypes of technologies.
The data sheets are continuously updated as technologies evolve, when data changes significantly or if errors are found.
On the left is an index of the technologies in short name with links to the relevant sheets. Below are the technologies with further descriptions.
INDEX:
01 Supercritical Pulverized Fuel Power Plant - Coal fired - Pulverized coal fired, subcritical steam process, condensing plant - Pulverized coal fired, supercritical steam process, condensing plant - Pulverized coal fired, ultra-supercritical steam process, condensing plant 02 Gas turbines
- Open cycle, backpressure
- Combined cycle, condensing
- Gas engine
03 Biomass power plants
04 Wind turbines, on-shore
05 Wind turbines, off-shore
06 Photovoltaics - Large scale Utility scale - Rooftop
07 Hydro Power Plants - Run-of-river without storage (small and large) - Run-of-river with storage (small and large) - Reservoir (small) - Reservoir (large) - Pumped storage (on-river) - Pumped storage (closed loop)
08 Nuclear Power Plant - Pressurized heavy-water reactor - Light-ater reactor
09 Battery storage
The technologies that might be included in the technology catalogue vary in terms of characteristics and it is therefore necessary to adopt the data inputs according to the specific technology.

## 01a Coal, subcritical
Technology | 01a Pulverized coal fired, subcritical steam process, condensing plant
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 210-600
Electricity efficiency, condensation mode, gross (%), name plate | 35.89 | 35.89 | 36 | 37 | 35 | 37 |  |  | A, B, C, D | 1, 2
Gross Heat rate at 55% loading (MCal/MWh) | 5,6% increase | [7 empty] | E, I | 3
Gross Heat Rate at 65% loading (MCal/MWh) | 2,5% increase | [7 empty] | E, I | 3
Gross Heat Rate at 75% loading (MCal/MWh) | 0,5% increase | [7 empty] | E, I | 3
Gross Heat Rate at 100 % loading (MCal/MWh) | 2396.2106 | 2396.2106 | 2388.8889 | 2324.3243 | 2457.1429 | 2324.3243 |  |  | A, B | 2
Auxiliary Power Consumption (%) | 7.5 |  |  |  | 5.75 | 8.5 |  |  | K | 10
Forced outage (%) | 10 | [8 empty] | 5
Planned outage (weeks per year) | 2.34 | [8 empty] | 6
Technical lifetime (years) | 25 | 25 | 30 | 30 | [5 empty] | 2, 4, 11, 12, 13
Construction time (years) | 3-4 | 3-4 | 3-4 | 3-4 | [5 empty] | 4
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Minimum load without secondary fuel support (% of full load) | 55 |  |  |  | 50 | 75 |  |  | F | 8, 9
Ramp Up Rate (% of Full Load/Minute) | 1 | [7 empty] | J | 3
Ramp Down Rate (% of Full Load/Minute) | 1 | [7 empty] | J | 3
Minimum Up time (hours) | 6 | [8 empty] | 7
Minimum Down time (hours) | 4 | [8 empty] | 7
Hot start-up time (hours) | 2-3 | [8 empty] | 3
Warm start-up time (hours) | 3-5 | [8 empty] | 3
Cold start-up time (hours) | 5-10 | [8 empty] | 3
Hot Start-up fuel consumption (Mcal/MW) | 600 | [8 empty] | 3
Warm Start-up fuel consumption (Mcal/MW) | 1000 | [8 empty] | 3
Cold Start-up fuel consumption (Mcal/MW) | 1800 | [8 empty] | 3
Environment
SO2 (mg/Nm^3 fuel) | 100 | [7 empty] | G | 14
NOX (mg/Nm^3 fuel) | 100 | [7 empty] | G | 14
Standard Particulate Matter (mg/Nm^3 fuel) | 30 | [7 empty] | G | 14
Financial data (in 2020₹)
Capital cost (cr. ₹/MW) | 9.2 | 9.1403 | 9.1562 | 9.1732 |  |  | 9.1374 | 9.2 | H | 2
- of which equipment (%)
- of which installation (%)
Fixed O&M ( cr. ₹/MW/year) | 0.2661 | 0.25938 | 0.25938 | 0.26532 | 0.2026 | 0.3296 |  |  |  | 4
Variable O&M (₹/MWh)
Hot Startup cost (cr. ₹/MW/startup) | 25000 | [8 empty] | 3
Warm Startup cost (cr. ₹/MW/startup) | 30000 | [8 empty] | 3
Cold Startup cost (cr. ₹/MW/startup) | 52000 | [8 empty] | 3
References
1) CEA Regulations (Technical Standards for Construction of Electrical Plants and Electric Lines), 2010
2) Inputs based on internal information in CEA and stakeholder inputs
3) Flexible Operation of Thermal Power Plant for Integration of Renewable Generation, Central Electricity Authority, 2019
4) CERC Regulations (Terms and Conditions of Tariff), 2019
5) National Electricity Plan Vol I - Generation, Central Electricity Authority, 2018
6) Review of performance of thermal power stations 2017-18, Central Electricity Authority, 2020
7) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
8) Indian Electricity Grid Code Regulations (Fourth Amendment), CERC, 2016
9) Reserve regulation ancillary services: half year analysis and feedback, POSOCO, 2016
10) Values based on stakeholder inputs
11) Technology Data – Generation of Electricity and District Heating; Danish Energy Agency, Energinet; 2020
12) Viet Nam Technology Catalogue – Technology data input for power system modelling in Viet Nam; EREA, Institute of Energy, Ea Energy Analyses, Danish Energy Agency, Danish Embassy in Vietnam, 2019
13) Technology data for the Indonesian Power Sector – Catalogue for Generation and Storage of Electricity; National Energy Council, Danish Energy Agency, Ea Energy Agency, Danish Embassy in Indonesia; 2017
14) Environment (Protection) Amendment Rules (MoEF&CC : Dec 2015)
Notes
A) Considering the boiler efficiency as 86%
B) The gross design Heat rate and gross Efficiency is based on HHV basis
C) Considering the Generator efficiency as 99%
D) Based on operating values
E) Defined as increase in net heat rate for a 200/210 MW unit
F) The central estimate is based on the normative value for central plants according to Indian regulation rather than actual operational data. The 75% is based on operational values.
G) Environmental norms for thermal power stations
H) Input supported by a number of Indian and international sources
I) Heat rates according to Indian grid code norms are 6% increase at 55% loading, 4% loading at 65% loading and 2.25% at 75% loading
J) According to Indian regulation (ref 1), the ramp up/down norms are 3% of Full Load//minute
K) As per CERC tariff regulation, 2019 lower bound should be 5.75

## 01b Coal, supercritical
Technology | 01b Pulverized coal fired, supercritical steam process, condensing plant
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 660-800 |  |  |  | 660 | 800
Electricity efficiency, condensation mode, gross (%), name plate | 38.1 | 39 | 40 | 41 | 38 | 40 |  |  | A, B, C, D | 1
Gross Heat rate at 55% loading (MCal/MWh) | 5.2% increase | [7 empty] | E, L | 1
Gross Heat Rate at 65% loading (MCal/MWh) | 3.4% increase | [7 empty] | E, L | 1
Gross Heat Rate at 75% loading (MCal/MWh) | 2.0% increase | [7 empty] | E, L | 1
Gross Heat Rate at 100 % loading (MCal/MWh) | 2257.2178 | 2205.1282 | 2150 | 2097.561 | 2263.1579 | 2150 |  |  | A, B | 1
Auxiliary Power Consumption (%) | 6.5 |  |  |  | 5.75 | 8 |  |  | F, N | 1
Forced outage (%) | 10 | [8 empty] | 5
Planned outage (weeks per year) | 2.34 | [8 empty] | 5
Technical lifetime (years) | 25 | 25 | 30 | 30 | [5 empty] | 1, 3, 10, 11, 12
Construction time (years) | 4 | 4 | 4 | 4 | [5 empty] | 3
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Minimum load without secondary fuel support (% of full load) | 55 |  |  |  | 50 | 75 |  |  | K | 7, 8
Ramp Up Rate (% of Full Load/Minute) | 1 | [7 empty] | M | 2
Ramp Down Rate (% of Full Load/Minute) | 1 | [7 empty] | M | 2
Minimum Up time (hours) | 6 | [8 empty] | 6
Minimum Down time (hours) | 4 | [8 empty] | 6
Hot start-up time (hours) | 2-3 | [8 empty] | 2
Warm start-up time (hours) | 3-5 | [8 empty] | 2
Cold start-up time (hours) | 5-10 | [8 empty] | 2
Hot Start-up fuel consumption (Mcal/MW) | 600 | [7 empty] | G | 2
Warm Start-up fuel consumption (Mcal/MW) | 1000 | [7 empty] | G | 2
Cold Start-up fuel consumption (Mcal/MW) | 1800 | [7 empty] | G | 2
Environment
SO2 (mg/Nm^3 fuel) | 100 | [7 empty] | I | 4
NOX (mg/Nm^3 fuel) | 100 | [7 empty] | I | 4
Standard Particulate Matter (mg/Nm^3 fuel) | 30 | [7 empty] | I | 13
Financial data (in 2020₹)
Capital cost (cr. ₹/MW) | 8.3 | 8.2461 | 8.2605 | 8.2758 | 7.6 | 8.7 | 7.58 | 8.67 | H | 1
- of which equipment (%)
- of which installation (%)
Fixed O&M (cr. ₹/MW/year) | 0.2026 | 0.19748 | 0.19654 | 0.19564 | [5 empty] | 3
Variable O&M (₹/MWh)
Hot Startup cost (₹/MW/startup) | 25000 | [7 empty] | J | 2
Warm Startup cost (₹/MW/startup) | 30000 | [7 empty] | J | 2
Cold Startup cost (₹/MW/startup) | 52000 | [7 empty] | J | 2
References
1) Inputs based on internal information in CEA and stakeholder inputs
2) Flexible Operation of Thermal Power Plant for Integration of Renewable Generation, Central Electricity Authority, 2019
3) CERC Regulations (Terms and Conditions of Tariff), 2019
4) National Electricity Plan Vol I - Generation, Central Electricity Authority, 2018
5) Review of performance of thermal power stations 2017-18, Central Electricity Authority, 2020
6) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
7) Indian Electricity Grid Code Regulations (Fourth Amendment), CERC, 2016
8) Reserve regulation ancillary services: half year analysis and feedback, POSOCO, 2016
9) CEA Regulations (Technical Standards for Construction of Electrical Plants and Electric Lines), 2010
10) Technology Data – Generation of Electricity and District Heating; Danish Energy Agency, Energinet; 2020
11) Viet Nam Technology Catalogue – Technology data input for power system modelling in Viet Nam; EREA, Institute of Energy, Ea Energy Analyses, Danish Energy Agency, Danish Embassy in Vietnam, 2019
12) Technology data for the Indonesian Power Sector – Catalogue for Generation and Storage of Electricity; National Energy Council, Danish Energy Agency, Ea Energy Agency, Danish Embassy in Indonesia; 2017
13) Environment (Protection) Amendment Rules (MoEF&CC: Dec 2015)
Notes
A) Considering the boiler efficiency as 86%
B) The gross design Heat rate and gross Efficiency is based on HHV basis
C) Considering the Generator efficiency as 99%
D) Based on operating values
E) Defined as increase in net heat rate for a 660 MW unit
F) Turbine driven BFP/ Motor driven BFP based auxiliary consumption
G) Defined as oil consumption for a 500 MW unit
H) Input supported by a number of Indian and international sources
I) Environmental norms for thermal power stations
J) Defined as increase in O&M costs for a 500 MW unit
K) This is based on the normative value for central plants according to Indian regulation rather than actual operational data
L) Heat rates according to Indian grid code norms are 6% increase at 55% loading, 4% loading at 65% loading and 2.25% at 75% loading
M) According to Indian regulation, the ramp up/down norms are 3% of Full Load//minute
N) As per CERC tariff regulation, 2019 lower bound should be 5.75

## 01c Coal, ultra-supercritical
Technology | 01c Pulverized coal fired, ultra-supercritical steam process, condensing plant
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 660-800 |  |  |  | 660 | 800
Electricity efficiency, condensation mode, gross (%), name plate | 41.3 | 41.8 | 42 | 43 | 39.6 | 43 |  |  | A | 1
Gross Heat rate at 55% loading (MCal/MWh) | 6.0% increase | [8 empty] | 2
Gross Heat Rate at 65% loading (MCal/MWh) | 3.9% increase | [8 empty] | 2
Gross Heat Rate at 75% loading (MCal/MWh) | 2.3% increase | [8 empty] | 2
Gross Heat Rate at 100 % loading (MCal/MWh) | 2082.3245 | 2057.4163 | 2047.619 | 2000 | 2171.7172 | 2000 |  |  |  | 1, 2
Auxiliary Power Consumption (%) | 6.5 |  |  |  | 5,75 | 8 |  |  | F, G | 1
Forced outage (%) | 10 | [8 empty] | 4
Planned outage (weeks per year) | 2.34 | [8 empty] | 3
Technical lifetime (years) | 25 | 25 | 30 | 30 | [5 empty] | 2, 5, 6, 7
Construction time (years) | 4 | 4 | 4 | 4 | [5 empty] | 11
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Minimum load without secondary fuel support (% of full load) | 55 | [7 empty] | B | 8
Ramp Up Rate (% of Full Load/Minute) | 1 | [7 empty] | E | 9
Ramp Down Rate (% of Full Load/Minute) | 1 | [7 empty] | E | 9
Minimum Up time (hours) | 6 | [8 empty] | 2
Minimum Down time (hours) | 4 | [8 empty] | 2
Hot start-up time (hours) | 2-3 | [8 empty] | 9
Warm start-up time (hours) | 3-5 | [8 empty] | 9
Cold start-up time (hours) | 5-10 | [8 empty] | 9
Hot Start-up fuel consumption (Mcal/MW) | 600 | [8 empty] | 9
Warm Start-up fuel consumption (Mcal/MW) | 1000 | [8 empty] | 9
Cold Start-up fuel consumption (Mcal/MW) | 1800 | [8 empty] | 9
Environment
SO2 (mg/Nm^3 fuel) | 100 | [7 empty] | C | 4
NOX (mg/Nm^3 fuel) | 100 | [7 empty] | C | 4
Standard Particulate Matter (mg/Nm^3 fuel) | 30 | [7 empty] | C | 10
Financial data (in 2020₹)
Capital cost (cr. ₹/MW) | 8.4 | 8.3455 | 8.36 | 8.3755 |  |  |  |  | D | 1
- of which equipment (%)
- of which installation (%)
Fixed O&M (cr. ₹/MW/year) | 0.2026 | 0.19748 | 0.19654 | 0.19564 | 0.1823 | 0.3296 |  |  |  | 11
Variable O&M (₹/MWh)
Hot Startup cost (₹/MW/startup)
Warm Startup cost (₹/MW/startup)
Cold Startup cost (₹/MW/startup)
References
1) Inputs based on internal information in CEA and stakeholder inputs
2) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
3) Review of performance of thermal power stations 2017-18, Central Electricity Authority, 2020
4) National Electricity Plan Vol I - Generation, Central Electricity Authority, 2018
5) Technology Data – Generation of Electricity and District Heating; Danish Energy Agency, Energinet; 2020
6) Viet Nam Technology Catalogue – Technology data input for power system modelling in Viet Nam; EREA, Institute of Energy, Ea Energy Analyses, Danish Energy Agency, Danish Embassy in Vietnam, 2019
7) Technology data for the Indonesian Power Sector – Catalogue for Generation and Storage of Electricity; National Energy Council, Danish Energy Agency, Ea Energy Agency, Danish Embassy in Indonesia; 2017
8) Indian Electricity Grid Code Regulations (Fourth Amendment), CERC, 2016
9) Flexible Operation of Thermal Power Plant for Integration of Renewable Generation, Central Electricity Authority, 2019
10) Environment (Protection) Amendment Rules (MoEF&CC: Dec 2015)
11) Central Electricity Regulatory Commission (Terms and Conditions of Tariff) Regulations, 2019
Notes
A) Based on operating values
B) This is based on the normative value for central plants according to Indian regulation rather than actual operational data
C) Environmental norms for thermal power stations
D) Data only based on few plants
E) According to Indian regulation, the ramp up/down norms are 3% of Full Load//minute
F) As per CERC tariff regulation, 2019 lower bound should be 5.75
G) Turbine driven BFP based auxiliary consumption

## 02a Gas turb. open cycle
Technology | 02a Gas turbine, open cycle (large), back pressure
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 50-200+ |  |  |  | 10 | 200+ |  |  | A | 1
Electricity efficiency, condensation mode, gross (%), name plate | 28 | 30 | 32 | 34 | 28 | 32 |  |  | B, C | 1, 5, 6, 7
Gross Heat rate at 55% loading (MCal/MWh) | 3277 | [8 empty] | 2
Gross Heat Rate at 65% loading (MCal/MWh)
Gross Heat Rate at 75% loading (MCal/MWh)
Gross Heat Rate at 100 % loading (MCal/MWh) | 3071.4286 | 2866.6667 | 2687.5 | 2529.4118 | 3071.4286 | 2687.5 |  |  |  | 1
Auxiliary Power Consumption (%) | 1 | [8 empty] | 1
Forced outage (%) | 2 | [7 empty] | D | 5, 6, 7
Planned outage (weeks per year) | 3 | [8 empty] | 10
Technical lifetime (years) | 25 | [8 empty] | 1, 10
Construction time (years) | 1.5 | [8 empty] | 10
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute) | 22 |  |  |  | 22 | 50 |  |  |  | 10
Minimum load without secondary fuel support (% of full load) | 55 | [7 empty] | E | 8, 9
Ramp Up Rate (% of Full Load/Minute) | 3 | [8 empty] | 4
Ramp Down Rate (% of Full Load/Minute) | 3 | [8 empty] | 4
Minimum Up time (hours) | 4 | [8 empty] | 2
Minimum Down time (hours) | 3 | [8 empty] | 2
Hot start-up time (hours)
Warm start-up time (hours)
Cold start-up time (hours)
Hot Start-up fuel consumption (Mcal/MW)
Warm Start-up fuel consumption (Mcal/MW)
Cold Start-up fuel consumption (Mcal/MW)
Environment
SO2 (mg/Nm^3 fuel)
NOX (mg/Nm^3 fuel)
Standard Particulate Matter (mg/Nm^3 fuel)
Financial data (in 2020₹)
Capital cost (cr. ₹/MW) | 5 | 5.0017 | 4.9715 | 4.9463 | 2.79 | 5.2 |  |  | F | 10
- of which equipment (%) | 80 | [8 empty] | 10
- of which installation (%) | 20 | [8 empty] | 10
Fixed O&M (cr. ₹/MW/year) | 0.1758 | 0.17586 | 0.1748 | 0.17391 |  |  |  |  | E | 3
Variable O&M (₹/MWh)
Hot Startup cost (₹/MW/startup) | 2473.0841 | [8 empty] | 10
Warm Startup cost (₹/MW/startup)
Cold Startup cost (₹/MW/startup)
References
1) Inputs based on internal information in CEA
2) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
3) CERC Regulations (Terms and Conditions of Tariff), 2019
4) CEA Regulations (Technical Standards for Construction of Electrical Plants and Electric Lines), 2010
5) Technology Data – Generation of Electricity and District Heating; Danish Energy Agency, Energinet; 2020
6) Viet Nam Technology Catalogue – Technology data input for power system modelling in Viet Nam; EREA, Institute of Energy, Ea Energy Analyses, Danish Energy Agency, Danish Embassy in Vietnam, 2019
7) Technology data for the Indonesian Power Sector – Catalogue for Generation and Storage of Electricity; National Energy Council, Danish Energy Agency, Ea Energy Agency, Danish Embassy in Indonesia; 2017
8) Indian Electricity Grid Code Regulations (Fourth Amendment), CERC, 2016
9) Reserve regulation ancillary services: half year analysis and feedback, POSOCO, 2016
10) Inputs based on stakeholder values
Notes
A) One unit configuration consists of 1 GTs
B) The gross design Heat rate and gross Efficiency is based on HHV basis
C) Considering the Generator efficiency as 99%
D) Based on international data
E) This is based on the normative value for central plants according to Indian regulation rather than actual operational data
F) Industrial gas turbines are more expensive than Utility size turbines. Utility Size turbines could be implemented at 40% lower price than Industrial turbines (10MW ~ 70MW size range)

## 02b Gas turb. combined cycle
Technology | 02b Gas turbine, combined cycle, condensing plant
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one module (MW) | 50-870 | 50-1000 | up to 1000 | up to 1000 | 50 | 870 |  |  | A
Electricity efficiency, condensation mode, gross (%), name plate | 60.45 | 62.45 | 64.45 | 66.45 | 58 | 63 |  |  | A, B, C, D | 1
Gross Heat rate at 55% loading (MCal/MWh) | 1614.356 | [8 empty] | 1
Gross Heat Rate at 65% loading (MCal/MWh) | 1591.694 | [8 empty] | 1
Gross Heat Rate at 75% loading (MCal/MWh) | 1527.304 | [8 empty] | 1
Gross Heat Rate at 100% loading (MCal/MWh) | 1422.6634 | 1377.1017 | 1334.3677 | 1294.2062 | 1365 | 1483 |  |  | B | 1
Auxiliary Power Consumption (%) | 2 | 2 | 2 | 2 |  |  |  |  | G | 1
Forced outage (%) | 0.75 | [8 empty] | 1
Planned outage (weeks per year) | 2 | [8 empty] | 1
Technical lifetime (years) | 25 | 25 | 25 | 25 | [5 empty] | 1
Construction time (years) | 2.5 | [8 empty] | 1
Regulation ability
Primary regulation (% per 30 seconds) | 1%/s ,max limit 10% of GT load | [8 empty] | 1
Secondary regulation (% per minute) | 10 | [8 empty] | 1
Minimum load without secondary fuel support (% of full load) | 55 | [7 empty] | E | 3
Ramp Up Rate (% of Full Load/Minute) | 11.5 | [8 empty] | 1
Ramp Down Rate (% of Full Load/Minute) | 11.5 | [8 empty] | 1
Minimum Up time (hours) | 4 | [8 empty] | 2
Minimum Down time (hours) | 3 | [8 empty] | 2
Hot start-up time (hours) | 0.75 | [8 empty] | 1
Warm start-up time (hours) | 1.5 | [8 empty] | 1
Cold start-up time (hours) | 2.3 | [8 empty] | 1
Hot Start-up fuel consumption (Mcal/MW) | 1700 | [8 empty] | 1
Warm Start-up fuel consumption (Mcal/MW) | 1750 | [8 empty] | 1
Cold Start-up fuel consumption (Mcal/MW) | 1900 | [8 empty] | 1
Environment
SO2 (mg/Nm^3 fuel)
NOX (mg/Nm^3 fuel)
Standard Particulate Matter (mg/Nm^3 fuel)
Financial data (in 2020₹)
Capital cost (cr. ₹/MW) | 3.4735 | 3.4747 | 3.4537 | 3.4362 | [5 empty] | 1
- of which equipment (%) | 80 | 0 | 0 | 0 | [5 empty] | 1
- of which installation (%) | 20 | 0 | 0 | 0 | [5 empty] | 1
Fixed O&M (cr. ₹/MW/year) | 0.28946 | 0.2864 | 0.29 | 0.286 |  |  |  |  | F | 1
Variable O&M (₹/MWh) | 0.20841 | 0.20621 | 0.21 | 0.21 | [5 empty] | 1
Hot Startup cost (₹/MW/startup) | 1556.3537 | [8 empty] | 1
Warm Startup cost (₹/MW/startup) | 7781.7687 | [8 empty] | 1
Cold Startup cost (₹/MW/startup) | 12450.83 | [8 empty] | 1
References
1) Values based on stakeholder inputs
2) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
3) Indian Electricity Grid Code Regulations (Fourth Amendment), CERC, 2016
Notes
A) Single module includes 1GT+1 ST/ 2GT+1ST/3GT+1ST
B) Value changes according to size of unit
C) The gross design Heat rate and gross Efficiency is based on HHV basis
D) Considering the Generator efficiency as 99%
E) This is based on the normative value for central plants according to Indian regulation rather than actual operational data
F) According to CERC tariff regulation the O&M should be 0.18 cr. ₹/MW/year
G) As per CERC tariff Regulation norms, 2019-24 it is 2.75%

## 02c Gas engine
Technology | 02c Gas Engine
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Notes | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 10 | 12 |  |  | 1 | 10
Electricity efficiency, condensation mode, gross (%), name plate | 46.03 | 48.27 | 49 | 50 |  |  |  |  | A | 1
Gross Heat rate at 55% loading (MCal/MWh) | [8 empty] | B
Gross Heat Rate at 65% loading (MCal/MWh) | [8 empty] | B
Gross Heat Rate at 75% loading (MCal/MWh) | [8 empty] | B
Gross Heat Rate at 100% loading (MCal/MWh) | 1868.3467 | 1781.6449 | 1755.102 | 1720 |  |  |  |  | B | 1
Auxiliary Power Consumption (%) | 2 | [8 empty] | 1
Forced outage (%) | 1 | [8 empty] | 1
Planned outage (weeks per year) | 1 | [8 empty] | 1
Technical lifetime (years) | 25 | 25 | 25 | 25 | [5 empty] | 1, 2
Construction time (years) | 1 | 1 | 1 | 1 | [5 empty] | 1, 2
Regulation ability
Primary regulation (% per 30 seconds) | 84 | 84 | [6 empty] | C | 1
Secondary regulation (% per minute) | 84 | 84 | [6 empty] | C | 1
Minimum load without secondary fuel support (% of full load) | 10 | 10 | [6 empty] | D | 1
Ramp Up Rate (% of Full Load/Minute) | 100 | 100 | [6 empty] | E | 1
Ramp Down Rate (% of Full Load/Minute) | 100 | 100 | [6 empty] | F | 1
Minimum Up time (hours) | 0 | 0 | [7 empty] | 1
Minimum Down time (hours) | 0.083333 | 0.083333 | [6 empty] | G | 1
Hot start-up time (hours) | 0.033333 | 0.033333 | [7 empty] | 1
Warm start-up time (hours) | 0.083333 | 0.083333 | [7 empty] | 1
Cold start-up time (hours) | 0.16667 | 0.16667 | [7 empty] | 1
Hot Start-up fuel consumption (Mcal/MW) | 287 | 287 | [6 empty] | H | 1
Warm Start-up fuel consumption (Mcal/MW) | 836 | 836 | [6 empty] | I | 1
Cold Start-up fuel consumption (Mcal/MW) | 1660 | 1660 | [6 empty] | J | 1
Environment
SO2 (mg/Nm^3 fuel)
NOX (mg/Nm^3 fuel) | 36-90 ppm @15% dry O2 available | [8 empty] | 1
Standard Particulate Matter (mg/Nm^3 fuel)
Financial data (in 2020₹)
Capital cost (cr. ₹/MW) | 4.1 | 4.1014 | 4.0766 | 4.056 | [5 empty] | 1
- of which equipment (%) | 97 | [8 empty] | 1
- of which installation (%) | 3 | [8 empty] | 1
Fixed O&M (cr. ₹/MW/year) | 0.073 | 0.073024 | 0.072608 | 0.071829 |  |  |  |  | K | 1
Variable O&M (₹/MWh) | 557 | 550.6645 | 553.8273 | 551.0175 | [5 empty] | 1, 2
Hot Startup cost (₹/MW/startup) | [8 empty] | L
Warm Startup cost (₹/MW/startup) | [8 empty] | L
Cold Startup cost (₹/MW/startup) | [8 empty] | L
References
1) Value based on inputs from Indian stakeholder
2) Technology Data – Generation of Electricity and District Heating; Danish Energy Agency, Energinet; 2020
Notes
A) Gross, Single Cycle, without Heat Recovery
B) Plant efficiency remains unchanged for all loading factors due to modularity.
C) Maximum genset specific loading rate for hot machine.
D) GEGs designed for continuous operation with primary fuel. No secondary fuel is needed
E) 2.8% per sec for engines which are operating for more than 15 min.
F) 4% per sec for engines which are operating for more than 15 min.
G) Required by exhaust gas ventilation before start-up
H) Corresponding to "2 minutes to full load" and meaning fuel consumption up to full load.
I) Corresponding to "5 minutes to full load" and meaning fuel consumption up to full load.
J) Corresponding to "10 minutes to full load" and meaning fuel consumption up to full load.
K) According to CERC tariff regulation the O&M should be 0.36 cr. ₹/MW/year
L) For reciprocating engines there is no additional start-up related costs. The technology is capable of achieving full load in under 5 min without any secondary fuel support and additional O&M cost.

## 03 Biomass extract. plant
Technology | 03 Biomass plant
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 10 | [8 empty] | 1
Electricity efficiency, condensation mode, gross (%), name plate | 26.5 |  |  |  | 24 | 28 |  |  |  | 1
Gross Heat rate at 55% loading (MCal/MWh) | 3440 |  |  |  | 3245 | 3660 |  |  |  | 1
Gross Heat Rate at 65% loading (MCal/MWh) | 3373 |  |  |  | 3185 | 3583 |  |  |  | 1
Gross Heat Rate at 75% loading (MCal/MWh) | 3308 |  |  |  | 3127 | 3510 |  |  |  | 1
Gross Heat Rate at 100% loading (MCal/MWh) | 3245 |  |  |  | 3071 | 3440 |  |  |  | 1
Auxiliary Power Consumption (%) | 10 |  |  |  | 8 | 12,5 |  |  |  | 1
Forced outage (%) | 10 |  |  |  | 3 | 15 |  |  |  | 1
Planned outage (weeks per year) | 3.5 |  |  |  | 2 | 5 |  |  |  | 1
Technical lifetime (years) | 20 |  |  |  | 15 | 25 |  |  |  | 1
Construction time (years) | 1.5 |  |  |  | 1.25 | 2 |  |  |  | 1
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Minimum load without secondary fuel support (% of full load) | 40 |  |  |  | 30 | 60 |  |  | A | 1
Ramp Up Rate (% of Full Load/Minute) | 0.1 | [8 empty] | 1
Ramp Down Rate (% of Full Load/Minute) | 0.2 | [8 empty] | 1
Minimum Up time (hours) | 2 |  |  |  | 1.5 | 3 |  |  |  | 1
Minimum Down time (hours) | 1 |  |  |  | 0.5 | 2 |  |  |  | 1
Hot start-up time (hours) | 1 |  |  |  | 0.75 | 1.5 |  |  | B | 1
Warm start-up time (hours) | 1.5 |  |  |  | 1.25 | 2 |  |  | B | 1
Cold start-up time (hours) | 2 |  |  |  | 1.5 | 3 |  |  | B | 1
Hot Start-up fuel consumption (Mcal/MW) | 3000 |  |  |  | 2250 | 4500 |  |  | B | 1
Warm Start-up fuel consumption (Mcal/MW) | 4500 |  |  |  | 3750 | 6000 |  |  | B | 1
Cold Start-up fuel consumption (Mcal/MW) | 6000 |  |  |  | 4500 | 9000 |  |  | B | 1
Environment
SO2 (mg/Nm^3 fuel)
NOX (mg/Nm^3 fuel)
Standard Particulate Matter (mg/Nm^3 fuel)
Financial data (in 2020₹)
Capital cost (cr. ₹/MW) | 5 | 5 | 4.9039 | 4.8291 | 4 | 5.5 |  |  |  | 1
- of which equipment (%) | 80 |  |  |  | 70 | 85 |  |  |  | 1
- of which installation (%) | 20 |  |  |  | 15 | 30 |  |  |  | 1
Fixed O&M (cr. ₹/MW/year) | 0.1 | 0.099183 | 0.098077 | 0.096582 |  |  |  |  | C | 2
Variable O&M (₹/MWh)
Hot Startup cost (₹/MW/startup) | 2217 |  |  |  | 1663 | 3325 |  |  | B | 1
Warm Startup cost (₹/MW/startup) | 3325 |  |  |  | 2771 | 4433 |  |  | B | 1
Cold Startup cost (₹/MW/startup) | 4433 |  |  |  | 3325 | 6650 |  |  | B | 1
References
1) Value based on inputs from Indian stakeholder
2) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
Notes
A) This is based on operational data. According to norms minimum load is 55% for central plants.
B) To reach 10 MW
C) As per CERC tariff regulation for RE, in 2020 it is 0.46Cr/MW/year

## 04 Onshore turbines
Technology | 04 Large wind turbines on land
Year of final investment decision | 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 2.5 | 4-5 | 6-8 | 8-10 | 2.2 | 2.5 |  |  |  | 1
Location-wise Capacity Utilization Factor (%) | 38 | 40 | 42 | 44 | 35 | 38 |  |  | A, B | 1
Forced outage (%) | 2.5 | 2 | 2 | 2 | 1 | 2.5 |  |  |  | 1
Planned outage (weeks per year) | 0.5 | 0.26071 | 0.26071 | 0.26071 | 0.26 | 0.5 |  |  |  | 1
Auxiliary Power Consumption (%) | 0.5 | 0.5 | 0.5 | 0.5 | [5 empty] | 1
Technical lifetime (years) | 25 | 30 | 30 | 30 | [5 empty] | 1
Construction time (years) | 1.5 | 1 | 1 | 1 | [5 empty] | 1
Space requirement (1000m2/MW) | 14 | 14 | 14 | 14 | [5 empty] | 1
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 6.6601 | 6.2356 | 6.0434 | 5.9123 | 6 | 7.7 |  |  |  | 1
- of which equipment (%) | 63.8734 | 62.1055 | 60.5268 | 60.1024 |  |  |  |  | C | 2
- of which installation/development (%) | 8.125 | 7.9001 | 7.6993 | 7.6453 |  |  |  |  | C | 2
- of which is related to grid connection (%) | 4.7619 | 4.8873 | 5.1773 | 5.2552 |  |  |  |  | C | 2
- of which is related to rent of land (%) | 7.5976 | 8.2081 | 8.6951 | 8.826 |  |  |  |  | C | 2
- of which is related to other costs (i.e. compensation of neighbours, etc.) (%) | 12.4243 | 13.4227 | 14.219 | 14.4331 |  |  |  |  | C | 2
Fixed O&M (cr. ₹/MW/year) | 0.068182 | 0.064 | 0.062 | 0.061 | [5 empty] | 1
Variable O&M (₹/MWh) | 240 | 225 | 218 | 213 | [5 empty] | 1
Technology specific data
Rotor diameter | 132 | 155 | 170 | 180 | 120 | 132 |  |  |  | 1
Hub height | 130 | 140 | 150 | 160 | 120 | 130 |  |  |  | 1
Specific power (W/m2) | 182.7774 | 238.605 | 308.5535 | 353.857 | [5 empty] | 1
Average capacity utilization factor (%) | 38 | 40 | 42 | 44 | 35 | 38 |  |  |  | 1
Average availability (%) | 96 | 97 | 97 | 97 | 95 | 96 |  |  |  | 1
References
1) Value based on inputs from Indian stakeholder
2) Technology Data – Generation of Electricity and District Heating; Danish Energy Agency, Energinet; 2020
Notes
A) This value is highly location specific and related to the size of the turbine
B) The data provided is for new, large turbines with hub heights around 130 m. Existing Indian onshore wind turbines with hub heights around 80 m would result in a lower CUF, possibly around 25% depending on location
C) This data is solely based on international experiences as no Indian data is available

## 05 Offshore turbines
Technology | 05 Large wind turbines offshore
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 8 | 15 | 18 | 20 | 4.2 | 8 | 15 | 30 | A, B | 1,2,3,4
Location-wise Capacity Utilization Factor (%) | 43 | 44-60 | 44-60 | 44-60 | 38 | 47.5 | 44 | 65 | D | 1
Electrical losses (%) | 5 | 5 | 5 | 5 |  |  |  |  | E | 1
Forced and planned outage (%) | 4 | 4 | 4 | 4 |  |  |  |  | C, E | 1
Technical lifetime (years) | 25 | 30 | 30 | 30 |  |  | 25 | 35 | B | 1,2,3,4
Development time (years) | 1.5 | 1.5 | 1.5 | 1.5 |  |  | 1.5 | 2 |  | 1
Construction time (years) | 2.5 | 2.5 | 2 | 2 |  |  | 1.5 | 2.5 |  | 1.3
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 23.1 | 13.8 | 12.66 | 11.97 |  |  |  |  | E | 1
- of which equipment (%) | 57.25 | [7 empty] | F | 1
- of which installation (%) | 18.88 | [7 empty] | F | 1
- of which grid connection (%) | 23.85 | [7 empty] | F | 1
Fixed O&M (cr. ₹/MW/year) | 0.674 | 0.364 | 0.323 | 0.298 |  |  |  |  | E | 1
Variable O&M (₹/MWh)
Technology specific data
Rotor diameter | 164 | 240 | 260 | 280 | [5 empty] | 1.3
Hub height | 103 | 150 | 160 | 170 | [5 empty] | 1.3
Specific power (W/m2) | 379 | 332 | 339 | 325 | [5 empty] | 1.3
Average availability (%) | 96 | 97 | 97 | 98
References:
1) Value based on inputs from offshore wind stakeholders and the FIMOI project
2) Technology data for the Indonesian Power Sector – Catalogue for Generation and Storage of Electricity; National Energy Council, Danish Energy Agency, Ea Energy Agency, Danish Embassy in Indonesia; 2017
3) Technology Data – Generation of Electricity and District Heating; Danish Energy Agency, Energinet; 2020
4) Viet Nam Technology Catalogue – Technology data input for power system modelling in Viet Nam; EREA, Institute of Energy, Ea Energy Analyses, Danish Energy Agency, Danish Embassy in Vietnam, 2019
Notes:
A) This value is highly location specific and related to the size of the turbine
B) Future projections based on international data
C) Potential curtailment not included
D) The span covers very diverse sea zones in both Tamil Nadu and Gujarat. The capacity factor is gross without electrical losses and forced or planned outages
E) Technical and financial data are based on a ‘full scope’ offshore wind farm, including wind farm and full transmission asset (offshore substation, export cables and onshore substation and cabling)
F) The category ‘equipment’ covers wind turbine, foundation and array cables; ‘installation’ covers project development and execution, and installation; ‘grid connection’ covers offshore substation, offshore and onshore cables and onshore substation

## 06a Photovoltaics Large
Technology | 06a Photovoltaics: Large scale utility systems
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 50-150 | 150-400 | 150-1000 | 150-2000 | 50 | 150 | 150 | 2000 |  | 1
Location-wise Capacity Utilization Factor (%) | 19.5 | 22 | 23 | 25 | 15 | 24 | 20 | 30 | A, B | 1
Forced outage (%) | 1.5 | 1 | 0.8 | 0.6 | 0.5 | 2 | 0.5 | 1 |  | 1 | 100
Planned outage (weeks per year) | 0 | 0 | 0 | 0 | [5 empty] | 1
Auxiliary Power Consumption (%) | 1 | 1 | 0.75 | 0.7 | 0.5 | 2 | 0.4 | 1 |  | 1
Technical lifetime (years) | 25 | 27.5 | 30 | 32.5 | 25 | 30 | 25 | 40 |  | 1
Construction time (years) | 0.75 | 0.5 | 0.5 | 0.5 | 0.5 | 1 | 0.4 | 0.5 |  | 1
Space requirement (1000m2/MW) | 14 | 12 | 10 | 8 | 7 | 21 | 4.5 | 10 |  | 1
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 5.4375 | 3.9027 | 2.69 | 2.274 | 3.5 | 6 | 1.4 | 4 |  | 1
- of which PV module (%) | 45 | 45 | 47 | 46 | 35 | 50 |  |  |  | 1
- of which inverter (%) | 15 | 15 | 10 | 10 | 0.051429 | 15 |  |  |  | 1
- of which transformer and grid connection (%) | 10 | 10 | 5 | 5 | 5 | 10 |  |  |  | 1
- of which installation (%) | 20 | 20 | 21 | 21 | 0.042857 | 20 |  |  |  | 1
- of which is related to other costs (i.e. residual balance of plant, mark-up & contingency cost) (%) | 10 | 10 | 17 | 18 | 5 | 0.34857 |  |  |  | 1
Fixed O&M (cr. ₹/MW/year) | 0.035 | 0.022328 | 0.016744 | 0.011872 | 0.03 | 0.035 | 0.010744 | 0.013 |  | 1
- of which is rent of land | 15000 | 20000 | 25000 | 25000 | [5 empty] | 1
Financial data (in 2020₹) per installed peak capacity
Capital Cost (cr. ₹/MWp) | 4.1067 | 2.8929 | 2.0316 | 1.7 | 2.64 | 4.2133 | 1.2 | 3 |  | 1 | 10000000
- of which PV module (%) | 45 | 45 | 47 | 46 | 35 | 50 |  |  |  | 1
- of which inverter (%) | 15 | 15 | 10 | 10 | 7 | 15 |  |  |  | 1
- of which transformer and grid connection (%) | 10 | 10 | 5 | 5 | 5 | 10 |  |  |  | 1
- of which installation (%) | 20 | 20 | 21 | 21 | 6 | 20 |  |  |  | 1
- of which is related to other costs (i.e. residual balance of plant, mark-up & contingency cost) (%) | 10 | 10 | 17 | 18 | 5 | 30 |  |  |  | 1
Fixed O&M (cr. ₹/MWp/year) | 0.035 | 0.024656 | 0.017487 | 0.015 | 0.03 | 0.035 | 0.010744 | 0.013 |  | 1
- of which is rent of land | 15000 | 20000 | 25000 | 25000 | [5 empty] | 1
Technology-specific data
Global horizontal irradiance (kWh/m2/year) | 1900 - 2100 | 1900 - 2100 | 1900 - 2100 | 1900 - 2100 |  |  |  |  | C | 1
Generating capacity for one unit (MWp)
Average annual peak power full-load hours (MWh/MWp) | 1576.8 | 1734.48 | 1821.204 | 1912.2642 | [5 empty] | 1
Average annual degradation of full-load hours (%) | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.5 | 0.7 |  | 1
DC/ACMAX sizing factor (Wp/Wac) | 1.2-1.5/1.0 | 1.2-1.5/1.0 | 1.2-1.5/1.0 | 1.2-1.5/1.0 | 1.2/1.0 | 1.5/1.0 | 1.2/1.0 | 1.5/1.0 |  | 1
Transposition Factor (fixed tilt system) | 1.17 | [8 empty] | 1
Performance ratio (measure of combined losses) | 0.8 | 0.82 | 0.83 | 0.84 | 0.78 | 0.8 | 0.82 | 0.85 |  | 1
PV module conversion efficiency (%) | 19 | 22 | 23 | 25 | 19 | 21 | 25 | 26 |  | 1
Inverter lifetime (years) | 10 | 10 | 10 | 15 | 5 | 10 | 10 | 20 |  | 1
Space requirement (1000m2/MWp) | 10 | 8.57 | 7.14 | 5.71 | 8 | 16 |  |  |  | 1
References
1) Value based on inputs from various Indian stakeholders
Notes
A) This value is highly location specific
B) Based on sizing factor 1:1
C) This value is according to satellite data as local factors such as cloud cover, pollution, etc. will impact the value

## 06b Photovoltaics rooftop
Technology | 06b Photovoltaics: Rooftop System
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 0,5-5 |  |  |  | 0.3 | 5 |  |  |  | 1
Location-wise Capacity Utilization Factor (%) | 18.5 | 21 | 22 | 23 | 15 | 22 | 20 | 30 | A | 1
Forced outage (%) | 5 | 3 | 2.5 | 2 | 0.5 | 9 | 2 | 2.5 | B | 1
Planned outage (weeks per year) | 1.13 | 0.57143 | 0.28571 | 0.22143 | 0.26 | 4 | 0.14 | 0.3 |  | 1
Auxiliary Power Consumption (%) | 1 | 0.6 | 0.5 | 0.4 | 1 | 3 | 0 | 0.4 |  | 1
Technical lifetime (years) | 25 | 27.5 | 30 | 32.5 | 25 | 25 | 25 | 40 |  | 1
Construction time (years) | 0.5 | 0.39167 | 0.325 | 0.3 | 0.5 | 2 | 0.25 | 0.35 |  | 1
Space requirement (1000m2/MW) | 9.5 | 9 | 7.5 | 6.25 | 5 | 14 | 4.5 | 8 | A | 1
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 4.3093 | 3.093 | 2.1319 | 1.8022 | 3.96 | 5 | 0.13 | 4 |  | 1
- of which PV module (%) | 51 | 46.5 | 43.5 | 43.5 | 45 | 58 | 40 | 47 |  | 1
- of which inverter (%) | 22 | 20 | 22.5 | 22.5 | 20 | 22 | 20 | 25 |  | 1
- of which transformer and grid connection (%) | 7 | 8 | 8 | 8 | 6 | 10 | 6 | 10 |  | 1
- of which installation (%) | 10 | 15 | 15 | 15 | 1 | 20 | 10 | 20 |  | 1
- of which is related to other costs (i.e. residual balance of plant, mark-up & contingency cost) (%) | 10 | 10.5 | 11 | 11 | 5 | 14 | 5 | 17 |  | 1
Fixed O&M (cr. ₹/MW/year) | 0.046453 | 0.032724 | 0.02321 | 0.019 | 0.03 | 0.07936 | 0.01426 | 0.035 |  | 1
Financial data (in 2020₹) per installed peak capacity | [10 empty] | 10000000
Capital Cost (cr. ₹/MWp) | 3.856 | 2.8 | 1.9266 | 1.6 | 3.6 | 4 | 1.1 | 3 |  | 1
- of which PV module (%) | 51 | 46.5 | 43.5 | 43.5 | 45 | 58 | 40 | 47 |  | 1
- of which inverter (%) | 22 | 20 | 22.5 | 22.5 | 20 | 22 | 20 | 25 |  | 1
- of which transformer and grid connection (%) | 7 | 8 | 8 | 8 | 6 | 10 | 6 | 10 |  | 1
- of which installation (%) | 10 | 15 | 15 | 15 | 1 | 20 | 10 | 20 |  | 1
- of which is related to other costs (i.e. residual balance of plant, mark-up & contingency cost) (%) | 10 | 10.5 | 11 | 11 | 5 | 14 | 5 | 17 |  | 1
Fixed O&M (cr. ₹/MWp/year) | 0.051453 | 0.037 | 0.025 | 0.022 | 0.03 | 0.07936 | 0.01426 | 0.035 |  | 1
Technology-specific data
Global horizontal irradiance (kWh/m2/year) | 1900 - 2100 | 1900 - 2100 | 1900 - 2100 | 1900 - 2100 |  |  |  |  | C | 1
Generating capacity for one unit (MWp) | 1 | [8 empty] | 1
Average annual peak power full-load hours (MWh/MWp)
Average annual degradation of full-load hours (%) | 0.7 | 0.7 | 0.6 | 0.5 | [5 empty] | 1
DC/ACMAX sizing factor (Wp/Wac) | 1.0-1.5/1.0 | 1.1-1.5/1.0 | 1.1-1.5/1.0 | 1.1-1.5/1.0 | 1.0/1.0 | 1.0/1.5 | 1.1/1.0 | 1.5/1.0 |  | 1
Transposition Factor (fixed tilt system)
Performance ratio (measure of combined losses) (%) | 77 | 81 | 82 | 83.5 | 75 | 80 | 82 | 85 |  | 1
PV module conversion efficiency (%) | 19 | 22 | 23 | 24 | 13 | 21 | 23 | 25 |  | 1
Inverter lifetime (years) | 10 | 10 | 12.5 | 15 | 5 | 10 | 10 | 20 |  | 1
Space requirement (1000m2/MWp) | 10 | 8.57 | 7.82 | 6.855 | 9.2 | 12.14 | 5.71 | 8
References:
1) Value based on inputs from various Indian stakeholders
Notes:
A) This value is highly location specific and specified for Standard Test Condition (STC)
B) This value will differentiate between rural and urban systems
C) This value is according to satellite data as local factors such as cloud cover, pollution, etc. will impact the value

## 07a Hydro, ROR wo storage
Technology | 07a Hydro power plants, Run-of-river without storage
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 35-120 |  |  |  | 35 | 120 |  |  |  | 1
Electricity efficiency, condensation mode, gross (%) | 97.2925 |  |  |  | 94 | 98 |  |  | A | 1
Forced outage (%) | 1 |  |  |  | 0.1 | 6 |  |  | B | 1,2
Planned outage (weeks per year) | 3.12 |  |  |  | 1.1 | 4.7 |  |  | B | 1,2
Auxiliary Power Consumption (%) | 0.6 |  |  |  | 0.6 | 2.11 |  |  |  | 1,2
Technical lifetime (years) | 40 | [8 empty] | 1
Construction time (years) | 6.9375 | [8 empty] | 1
Regulation ability
Ramp Up Rate (% of Full Load/Minute) | 58 |  |  |  | 20 | 90 |  |  |  | 1
Ramp Down Rate (% of Full Load/Minute) | 64 |  |  |  | 30 | 100 |  |  |  | 1
Primary load support (% per 30 seconds) | 37.8 |  |  |  | 10 | 60 |  |  |  | 1
Secondary load support (% per minute) | 58 |  |  |  | 20 | 90 |  |  |  | 1
Minimum load (% of full load) | 33.769 |  |  |  | 5 | 60 |  |  |  | 1
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 10.7 | 10.6529 | 10.6295 | 10.6092 | 5.9 | 17.1 |  |  | B | 3
- of which equipment (%) | 18.1324 | [8 empty] | 1
- of which installation/development (%) | 79.9187 | [8 empty] | 1
- of which is related to rent of land (%) | 1.658 | [7 empty] | C | 1
- of which is related to other costs (i.e. compensation of neighbours, etc.) (%) | 0.2909 | [8 empty] | 1
Fixed O&M (cr. ₹/MW/year) | 0.44096 | 0.44 | 0.44 | 0.44 | 0.20554 | 1.1168 |  |  |  | 1
Variable O&M (₹/MWh)
References
1) Value based on inputs from Indian stakeholder, including four local plants from Northern region
2) Hydro Review, CEA, 2019
3) CEA, Project monitoring - Quarterly review No. 104 (Jan-Mar 2021), 2021
Notes
A) As per the name plate efficiency of the equipment
B) Values changes according to plants and the uncertainty ranges are therefore rather large. Data for under-construction plants.
C) Land + Capitalized Value of Abatement of Land Revenue

## 07b Hydro, ROR with storage
Technology | 07b Hydro power plants, ROR with storage
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 20-250 |  |  |  | 20 | 250 |  |  |  | 1
Electricity efficiency, condensation mode, gross (%) | 98.4248 | [7 empty] | A | 1
Forced outage (%) | 3.5 |  |  |  | 0.06 | 6 |  |  | B | 1,2
Planned outage (weeks per year) | 3.12 |  |  |  | 2.5 | 27.6 |  |  | B | 1,2
Auxiliary Power Consumption (%) | 0.7 |  |  |  | 0.6 | 1.4307 |  |  |  | 1
Technical lifetime (years) | 40 | [8 empty] | 1
Construction time (years) | 7.7222 |  |  |  | 3 | 11 |  |  |  | 1
Regulation ability
Ramp Up Rate (% of Full Load/Minute) | 58.1448 |  |  |  | 13.8889 | 100 |  |  |  | 1
Ramp Down Rate (% of Full Load/Minute) | 60.2897 |  |  |  | 13.8889 | 100 |  |  |  | 1
Primary load support (% per 30 seconds) | 35.7493 |  |  |  | 6.9444 | 100 |  |  |  | 1
Secondary load support (% per minute) | 58.0371 |  |  |  | 13.8889 | 100 |  |  |  | 1
Minimum load (% of full load) | 23.4034 |  |  |  | 5.5556 | 60 |  |  |  | 1
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 11.9 | 11.8476 | 11.8216 | 11.799 | 6.2 | 21.9 |  |  | B | 3
- of which equipment (%) | 18.2021 |  |  |  | 10.2008 | 24.7872 |  |  |  | 1
- of which installation/development (%) | 79.105 |  |  |  | 68.2772 | 88.15 |  |  |  | 1
- of which is related to rent of land (%) | 1.1946 |  |  |  | 0.082364 | 4.7013 |  |  | C | 1
- of which is related to other costs (i.e. compensation of neighbours, etc.) (%) | 1.4983 |  |  |  | 0.0042039 | 3.482 |  |  |  | 1
Fixed O&M (cr. ₹/MW/year) | 0.41479 | 0.41 | 0.41 | 0.41 | 0.12727 | 0.88933 |  |  |  | 1
Variable O&M (₹/MWh) | [9 empty] | 1
References
1) Value based on inputs from Indian stakeholder, including 12 plants in Northern and Eastern regions
2) Hydro Review, CEA, 2019
3) CEA, Project monitoring - Quarterly review No. 104 (Jan-Mar 2021), 2021
Notes
A) As per the name plate efficiency of the equipment
B) Values changes according to plants and the uncertainty ranges are therefore rather large. Data for under-construction plants.
C) Land + Capitalized Value of Abatement of Land Revenue

## 07c Small hydro, res
Technology | 07c Small Hydro power plants, reservoir (<25 MW)
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 1-5 | [8 empty] | 1
Electricity efficiency, condensation mode, gross (%) | 45 |  |  |  | 30 | 92 |  |  |  | 1,2
Forced outage (%) | 3.5 |  |  |  | 1 | 6 |  |  | B | 3
Planned outage (weeks per year) | 3.12 | [7 empty] | B | 3
Auxiliary Power Consumption (%) | 1 | [8 empty] | 1
Technical lifetime (years) | 40 | [8 empty] | 1
Construction time (years) | 3 | [8 empty] | 1
Storage capacity (MWh)
Discharge time (h)
Regulation ability
Ramp Up Rate (% of Full Load/Minute) | 2.5 | [8 empty] | 1
Ramp Down Rate (% of Full Load/Minute) | 2.5 | [8 empty] | 1
Primary load support (% per 30 seconds)
Secondary load support (% per minute)
Minimum load (% of full load)
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 8.035 | 8.035 | 7.9959 | 7.9668 | 7.8 | 11 |  |  | C | 2
- of which equipment (%)
- of which installation/development (%)
- of which is related to rent of land (%)
- of which is related to other costs (i.e. compensation of neighbours, etc.) (%)
Fixed O&M (cr. ₹/MW/year) | 0.24 | 0.24 | 0.24 | 0.24 | 0.24 | 0.43 |  |  | B | 2
Variable O&M (₹/MWh)
References:
1) Value based on inputs from Indian stakeholder
2) CERC (Terms and Conditions for Tariff determination from Renewable Energy Sources) Regulations, 2017
3) Hydro Review, CEA, 2019
Notes:
A) As per the name plate efficiency of the equipment
B) Values changes according to plants and the uncertainty ranges are therefore rather large.
C) Data for this value is highly uncertain. As per the CERC tariff regulation for RE Projects its in the range of 7.8Cr/MW to 11cr/MW.

## 07d Large hydro, res
Technology | 07d Large Hydro power plants, reservoir (>25 MW)
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 35-200 |  |  |  | 35 | 200 |  |  |  | 1, 2, 3
Electricity efficiency, condensation mode, gross (%) | 96.9 | 96.9 | 96.9 | 96.9 |  |  |  |  | A | 1
Forced outage (%) | 1 |  |  |  | 0.6 | 6 |  |  | B | 1, 4
Planned outage (weeks per year) | 3.12 |  |  |  | 2.5 | 4.87 |  |  | B | 1, 4
Auxiliary Power Consumption (%) | 0.6 | [8 empty] | 1, 4
Technical lifetime (years) | 40 | [8 empty] | 1
Construction time (years) | 5 |  |  |  | 4 | 7 |  |  |  | 1
Storage capacity (MWh)
Discharge time (h)
Regulation ability
Ramp Up Rate (% of Full Load/Minute) | 30 |  |  |  | 2.5 | 50 |  |  |  | 1
Ramp Down Rate (% of Full Load/Minute) | 30 |  |  |  | 2.5 | 50 |  |  |  | 1
Primary load support (% per 30 seconds) | 15 | [8 empty] | 1
Secondary load support (% per minute) | 30 | [8 empty] | 1
Minimum load (% of full load) | 8.5714 |  |  |  | 0 | 15 |  |  |  | 1
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 8.3 | 8.2635 | 8.2453 | 8.2296 | 3.7 | 17.6 |  |  | B | 5
- of which equipment (%) | 9.3376 | [8 empty] | 1
- of which installation/development (%) | 87.7629 | [8 empty] | 1
- of which is related to rent of land (%) | 2.8995 | [8 empty] | 1
- of which is related to other costs (i.e. compensation of neighbours, etc.) (%) | 0 | [8 empty] | 1
Fixed O&M (cr. ₹/MW/year) | 0.90838 | 0.9 | 0.9 | 0.9 |  |  |  |  | B | 1
Variable O&M (₹/MWh)
References
1) Value based on inputs from Indian stakeholder
2) Viet Nam Technology Catalogue – Technology data input for power system modelling in Viet Nam; EREA, Institute of Energy, Ea Energy Analyses, Danish Energy Agency, Danish Embassy in Vietnam; 2019
3) Technology data for the Indonesian Power Sector – Catalogue for Generation and Storage of Electricity; National Energy Council, Danish Energy Agency, Ea Energy Agency, Danish Embassy in Indonesia; 2017
4) Hydro Review, CEA, 2019
5) CEA, Project monitoring - Quarterly review No. 104 (Jan-Mar 2021), 2021
Notes
A) As per the name plate efficiency of the equipment
B) Values changes according to plants and the uncertainty ranges are therefore rather large. Data for under-construction plants.

## 07e Hydro, Pumped on-river
Technology | 07e Hydro power plants, Pumped storage on-river
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW)
Electricity efficiency, condensation mode, gross (%)
Forced outage (%)
Planned outage (weeks per year)
Auxiliary Power Consumption (%)
Technical lifetime (years) | 40 | [8 empty] | 1
Construction time (years) | 8 | [8 empty] | 1
Storage capacity (MWh)
Charging efficiency (%) | 80 | 80 | [6 empty] | A | 1
Discharge time (h)
Regulation ability
Ramp Up Rate (% of Full Load/Minute) | 50 | [8 empty] | 1
Ramp Down Rate (% of Full Load/Minute) | 50 | [8 empty] | 1
Primary load support (% per 30 seconds)
Secondary load support (% per minute)
Minimum load (% of full load)
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 6 | 5.9428 | 5.9392 | 5.9358 | [5 empty] | 1
- of which equipment (%)
- of which installation/development (%)
- of which is related to rent of land (%)
- of which is related to other costs (i.e. compensation of neighbours, etc.) (%)
Fixed O&M (cr. ₹/MW/year) | 0.15 | 0.15 | 0.15 | 0.15 | [5 empty] | 1
Variable O&M (₹/MWh)
References:
1) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
Notes:
A) Round-trip efficiency

## 07f Hydro, Pumped closed loop
Technology | 07f Hydro power plants, Pumped storage closed loop
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW)
Electricity efficiency, condensation mode, gross (%)
Forced outage (%)
Planned outage (weeks per year)
Auxiliary Power Consumption (%)
Technical lifetime (years) | 40 | [8 empty] | 1
Construction time (years) | 8 | [8 empty] | 3
Storage capacity (MWh)
Charging efficiency (%) | 70 | [8 empty] | 2
Discharge time (h)
Regulation ability
Ramp Up Rate (% of Full Load/Minute) | 50 | [8 empty] | 1
Ramp Down Rate (% of Full Load/Minute) | 50 | [8 empty] | 1
Primary load support (% per 30 seconds)
Secondary load support (% per minute)
Minimum load (% of full load)
Financial data (in 2020₹)
Capital Cost (cr. ₹/MW) | 3.85 | 3.8133 | 3.811 | 3.8088 | 2 | 5.7 |  |  |  | 1
- of which equipment (%)
- of which installation/development (%)
- of which is related to rent of land (%)
- of which is related to other costs (i.e. compensation of neighbours, etc.) (%)
Fixed O&M (cr. ₹/MW/year) | 0.09625 | 0.095333 | 0.095275 | 0.09522 | [5 empty] | 1
Variable O&M (₹/MWh)
References:
1) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
2) Flexible Operation of Thermal Power Plant for Integration of Renewable Generation, Central Electricity Authority, 2019
3) Inputs based on internal information in CEA
Notes:
A) Round-trip efficiency

## 08a Nuclear, PHWR
Technology | 08a Nuclear power plant, Pressurized heavy-water reactor
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 460 |  |  |  | 220 | 700 |  |  |  | 1
Electricity efficiency, condensation mode, gross (%), name plate | 31 | [7 empty] | B | 2
Heat rate at 55% loading (MCal/MWh)
Heat Rate at 65% loading (MCal/MWh)
Heat Rate at 75% loading (MCal/MWh)
Heat Rate at max. loading (MCal/MWh) | 2777 | [8 empty] | 3
Auxiliary Power Consumption (%) | 10.78 |  |  |  | 10.2 | 11.75 |  |  |  | 1
Forced outage (%)
Planned outage (weeks per year) | 1.196 | [7 empty] | B | 4
Technical lifetime (years) | 30 | [7 empty] | A | 3
Construction time (years) | 6 |  |  |  | 5 | 11 |  |  |  | 1, 2, 3
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Minimum load without secondary fuel support (% of full load)
Ramp Up Rate (% of Full Load/Minute)
Ramp Down Rate (% of Full Load/Minute)
Minimum Up time (hours) | 6 | [8 empty] | 3
Minimum Down time (hours) | 4 | [8 empty] | 3
Hot start-up time (hours)
Warm start-up time (hours)
Cold start-up time (hours)
Hot Start-up fuel consumption (MCal)
Warm Start-up fuel consumption (MCal)
Cold Start-up fuel consumption (MCal)
Financial data (in 2020₹)
Capital cost (cr. ₹/MW) | 11.7 | 11.5931 | 11.5048 | 11.4476 | [5 empty] | 6
- of which equipment (%)
- of which installation (%)
Fixed O&M (cr. ₹/MW/year) | 0.4312 | 0.42726 | 0.4197 | 0.40774 | 0.2631 | 0.5993 |  |  |  | 5
Variable O&M (₹/MWh)
Hot Startup cost (₹/MW/startup)
Warm Startup cost (₹/MW/startup)
Cold Startup cost (₹/MW/startup)
References:
1) Value based on inputs from various Indian stakeholders
2) Technology Brief E03, IEA ETSAP, 2010
3) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
4) Least-cost pathways for India's electronic power sector, National Renewable Energy Laboratory; 2020
5) Department of Atomic Energy norms for determination of tariff for nuclear power plants
6) National Electricity Plan Vol I - Generation, Central Electricity Authority, 2018
Notes:
A) Examples of longer lifetimes in India exist. For example Tarapur 1&2 has operated for more than 50 years. NAPP 1&2 is being extended beyond 30 years.
B) Value based only on international sources

## 08b Nuclear, LWR
Technology | 08b Nuclear power plant, Light-water Reactor
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 1000-1600 |  |  |  | 1000 | 1600 |  |  |  | 1, 2
Electricity efficiency, condensation mode, gross (%), name plate | 31 | [7 empty] | A | 2
Heat rate at 55% loading (MCal/MWh)
Heat Rate at 65% loading (MCal/MWh)
Heat Rate at 75% loading (MCal/MWh)
Heat Rate at max. loading (MCal/MWh) | 2777 | [8 empty] | 3
Auxiliary Power Consumption (%) | 7.8 | [8 empty] | 1
Forced outage (%)
Planned outage (weeks per year)
Technical lifetime (years) | 30 | [8 empty] | 3
Construction time (years) | 6 |  |  |  | 5 | 11 |  |  |  | 1, 3
Regulation ability
Primary regulation (% per 30 seconds)
Secondary regulation (% per minute)
Minimum load without secondary fuel support (% of full load)
Ramp Up Rate (% of Full Load/Minute)
Ramp Down Rate (% of Full Load/Minute)
Minimum Up time (hours) | 6 | [8 empty] | 3
Minimum Down time (hours) | 4 | [8 empty] | 3
Hot start-up time (hours)
Warm start-up time (hours)
Cold start-up time (hours)
Hot Start-up fuel consumption (MCal)
Warm Start-up fuel consumption (MCal)
Cold Start-up fuel consumption (MCal)
Financial data (in 2020₹)
Capital cost (cr. ₹/MW) | 19 | 18.8265 | 18.51 | 18.11 | [5 empty] | 2, 3, 4
- of which equipment (%)
- of which installation (%)
Fixed O&M (cr. ₹/MW/year) | 0.25893 | 0.25657 | 0.25203 | 0.25 | [5 empty] | 5
Variable O&M (₹/MWh)
Hot Startup cost (₹/MW/startup)
Warm Startup cost (₹/MW/startup)
Cold Startup cost (₹/MW/startup)
References:
1) Value based on inputs from various Indian stakeholders
2) Technology Brief E03, IEA ETSAP, 2010
3) Report on Optimal Generation Capacity Mix for 2029-30; Central Electricity Authority, 2020
4) World Energy Outlook 2020, International Energy Agency, 2020
5) Department of Atomic Energy norms for determination of tariff for nuclear power plants
Notes:
A) Value based only on international sources

## 09 Battery storage, Li-ion
Technology | 09 Battery storage system (Lithium-ion)
| 2020 | 2030 | 2040 | 2050 | Uncertainty (2020) |  | Uncertainty (2050) |  | Note | Ref
Energy/technical data |  |  |  |  | Lower | Upper | Lower | Upper
Generating capacity for one unit (MW) | 1-100 | 1-200 | 1-300 | 1-500 | 1 | 100 | 1 | 500 |  | 1
Electricity efficiency, gross (%) | 90 | 92.5 | 94 | 94 | 88 | 92 | 90 | 98 | A | 1
Forced outage (%) | 1 | 0.5 | 0.5 | 0.5 | 0.4 | 1.3 | 0 | 1 |  | 1
Planned outage (weeks per year) | 1.5 | 1.5 | 1 | 1 | 1 | 2 | 1 | 1 |  | 1
Auxiliary Power Consumption (%) | 1 | 1 | 0.75 | 0.6 | 1 | 7.5 | 0.1 | 1 |  | 1
Technical inverter lifetime (years) | 16.6667 | 22.5 | 25 | 25 | 8 | 20 | 15 | 25 |  | 1
Lifetime (battery cycles) | 6000 | >8000 | ~10000 | ~20000 | 4500 | 8000 | 15000 | 20000 |  | 1
Construction time (years) | 0.86 | 0.5 | 0.33333 | 0.33333 | 0.75 | 2 | 0.16667 | 0.75 |  | 1
Storage capacity (MWh) | 1-200 | 1-800 | 1-1800 | 1132254 | 1-100 | 1-300 | 1-500 | 1-12000 | B | 1
Charging efficiency (%) | 95 | 96 | 97 | 97 | 95 | 94 | 96 | 99 | C | 1
Depth of Discharge (%) | 92.3333 | 94.75 | 98.5 | 98.5 | 80 | 80 | 95 | 100 |  | 1
Discharge time (h) | 2 | 4 | 6 | 10 | 1 | 4 | 6 | 12 |  | 1
Regulation ability
Primary load support (% per 30 seconds) | 100 | 100 | 100 | 100 | [5 empty] | 1
Secondary load support (% per minute) | 100 | 100 | 100 | 100 | [5 empty] | 1
Minimum load (% of full load) | 0 | 0 | 0 | 0 | [5 empty] | 1
Financial data (in 2020₹)
Capital cost
- per MWh basis (cr. ₹/MWh) | 2.375 | 1.37 | 1.19 | 1.09 | 1.125 | 2.5 | 0.5 | 1.2 | D | 1
- per MW basis (cr. ₹/MW) | 6.7333 | 3.8744 | 3.3792 | 3.0943 | 5 | 9 |  |  |  | 1
Fixed O&M (cr. ₹/MW/year) | 0.083333 | 0.054525 | 0.037923 | 0.04 | [5 empty] | 1
Variable O&M (₹/MWh) | 500000 | [8 empty] | 1
References:
1) Value based on inputs from various Indian stakeholders
Notes:
A) The DC efficiency of the system is 96.5%
B) Assuming number of hours of storage on basis of power capacity given
C) It is assumed a conversion from AC to DC and back to AC at the battery level.
D) Assuming 2 hours Storage in 2020, 4 hours Storage in 2030, 6 hours Storage in 2040 and 10 hours Storage in 2050